PUMP AUDIT REPORT

### Inspection Summary
- **Vibration**: 5.2 mm/s (Exceeds Acceptable Limit: 4.5 mm/s)
- **Bearing Temperature**: 82°C (Close to High-Temperature Alarm Limit: 85°C)
- **Seal Leakage**: 14 drops/min (Within Acceptable Limit: 5-20 drops/min)

### Recommendations
- **Action**: Immediate vibration spectrum analysis for P-104A.
- **Action**: Monitor bearing temperature closely and initiate lubrication schedule if necessary.
- **Action**: Continue to inspect the seal regularly and replace if leakage exceeds 20 drops/min.